CAlifornians for Renewable Energy, Inc.(CARE)

821 Lakeknoll Dr.

Sunnyvale, CA 94089

(408) 325-4690

STATE OF CALIFORNIA

Energy Resources Conservation

and Development Commission

In the Matter of:                           				) Docket No. 00-AFC-1

)

Application for Certification for the       			) Comments on the PSA&PDOC

Contra Costa Power Plant Project              			)

# comments on the contra costa power plant preliminary staff assessment& baaqmd preliminary determination of compliance

# Introduction and summary

## Introduction

CARE is currently participating as an intervenor in the Metcalf Energy Center (MEC) located in San Jose California. Coyote Valley Research Park (CVRP) is the development firm for the recently approved Coyote Research Park for CISCO Systems in South San Jose, a 1.3 billion dollar project, and is also an intervenor in the CCPP project. CVRP utilized expert consultants to prepare comments on the Bay Area Air Quality Management District’s (BAAQMD’s) Preliminary Determination of Compliance (PDOC). CARE has incorporated these comments (with additions and deletions). The emission control technology for the MEC, and the Contra Costa Power Project, is identical to that of the Delta Energy Center (DEC), which is 98-AFC-3 in the original complaint. Therefore the following comments apply to the Contra Costa Power Project (CCPP).

The key deficiencies in the PDOC and PSA are errors of omission. The PDOC does not contain a serious top-down BACT analysis (Section II, below). As a result it fails to correctly identify BACT for NOx (Section III), for CO (Section IV), for VOC (Section V), for startup emissions (Section VI), and their lack of negative PM10 impacts (Section VII).

The PDOC and PSA also lacks an adequate analysis of the toxics CCP would emit, emissions whose health consequences would easily exceed the CEC and BAAQMD thresholds for further analysis and mitigation (Section X).

Finally, CARE has commented on a variety of other matters ranging from the meteorological modeling in the PDOC to the treatment of the proposed on-site internal combustion engines to the proposed condition regarding overlapping startups of the two proposed CCPP turbines (Section XI).

BAAQMD application 27215 for authority to construct the Contra Costa Power Energy Center (CCPP) along with CEC 99-AFC-3 is the latest in a series of applications to build large new gas-fired combined cycle power plants which have come before the California Energy Commission (CEC) and various California air quality management districts (AQMDs).  Within the last year intervenors CARE and CURE, have pointed out that some of these projects are quite deficient in their BACT and other air quality analyses. CARE has participated as an intervenor in the Delta Energy Center. CARE has filed a complaint with the EPA Office of Civil Rights over the disparate impacts of air pollutants associated with this project. With these comments, CARE has identified a similar lengthy list of inadequacies in the PDOC for the CCPP proposal. CARE expects that the BAAQMD and the CEC will give serious attention to these inadequacies. Given the extensive scope of our comments, CARE calls upon the BAAQMD to re-circulate the PDOC for further comment after responding to our comments. To go directly to an FDOC and FSA at this stage would deny the public any substantive opportunity to comment on the many issues, which are inadequately addressed in this PDOC and the PSA, or not addressed at all.

## Summary of CARE’s comments

CARE’s comments have been grouped into a dozen main areas, which CARE summarized here. Within each area CARE have attempted to not only identify omissions or errors in the PDOC (e.g., the absence of a CO catalyst requirement) but also identify the position, which CARE believes the BAAQMD should adopt, and the facts supporting that position. CARE have also identified counter-arguments which the Applicant might make, or has already made elsewhere, and supplied the District with a response to those arguments.

The key deficiencies in the PDOC and PSA are errors of omission. The PDOC does not contain a serious top-down BACT analysis (Section II, below). As a result it fails to correctly identify BACT for NOx (Section III), for CO (Section IV), for VOC (Section VII), and for startup emissions (Section VIII). Along the way, the PDOC omits any discussion of other air quality benefits of catalyst-based CO and NOx control technologies (Section VI) and their lack of negative PM10 impacts (Section V).

The PDOC and PSA rely on Applicant data, which is either wrong or misleading, leading to inaccurate conclusions regarding PM10 emissions and offset requirements (Section IX).

The PDOC and PSA also lacks an adequate analysis of the toxics the CCPP would emit, emissions whose health consequences would easily exceed the CEC and BAAQMD thresholds for further analysis and mitigation (Section X).

Finally, CARE has commented on a variety of other matters ranging from the meteorological modeling in the PDOC to the treatment of the proposed on-site internal combustion engines to the proposed condition regarding overlapping startups of the two proposed CCPP turbines (Section XI).

# the pdoc does not include a top-down bact analysis

The project is a major source whose emissions trigger PSD requirements for NOx and CO.  (PDOC, Table 3.)  Any major modification subject to PSD must conduct an analysis to ensure that best available control technology ("BACT") is used.  This requirement is set forth in section 165(a)(4) of the federal Clean Air Act, in federal PSD regulations at 40 C.F.R. § 52.21(j), and in federal regulations providing the requirements for State implementation plan (SIP) approval of a State PSD program, at 40 C.F.R. § 51.166(j).  For PSD purposes, BACT is “an emissions limitation… based on the maximum degree of reduction for each pollutant subject to regulation under [the] Act which would be emitted from any proposed major stationary source….” (40 CFR § 52.21(b)(12).)

PSD regulations require the District, as EPA’s delegate, to perform and document an analysis to ensure that federal BACT is used.  (CAA, § 165(a)(4); 40 CFR 52.21(j).)  This obligation is fulfilled by conducting what is known as a “top-down BACT analysis” as outlined in EPA’s NSR Manual.  (NSR Manual, Chapter B.)  The NSR Manual and the top down procedure have been accepted by EPA’s Environmental Appeals Board (“EAB”) “as the most current statement of the Agency’s thinking on BACT issues” and are routinely used to decide cases involving matters of federal law. (See, e.g., Masonite Corporation, 5 E.A.D. 558 (EAB 1994); Inter-Power of New York, Inc.; 5 E.A.D. 135 (EAB 1994); Hawaiian Commercial & Sugar Company, 4 E.A.D. 99 (EAB 1992).)

The Environmental Appeals Board of the EPA has on several occasions stressed the primary importance of a complete and meaningful BACT analysis in the PSD program, stating most recently:

“The BACT analysis is one of the most critical elements of the PSD permitting process. As such, it should be well documented in the administrative record. A permitting authority's decision to eliminate potential control options as a matter of technical infeasibility, or due to collateral impacts, must be adequately explained and justified. See In re Masonite Corp., 5 E.A.D. 551, 566 (EAB 1994) (remanding PSD permit decision in part because BACT determination for one emission source was based on an incomplete cost-effectiveness analysis); In re Pennsauken County, N.J., Resource Recovery Facility, 2 E.A.D. 667, 672 (Adm'r 1988) (remanding PSD permit decision because “the applicant's BACT analysis does not contain the level of detail and analysis necessary to satisfy the applicant's burden” of showing that a particular control technology is technically or economically unachievable); Columbia Gulf, 2 E.A.D. at 830 (permit applicant and permit issuer must provide substantiation when rejecting the most effective technology).” In re Knauf Fiber Glass, GmbH, PSD Appeal Nos. 98-3 through 98-20 (EAB, Feb. 4, 1999).”

The top-down BACT process consists of five steps that are discussed in detail in Section B of the NSR Manual.  These steps are (NSR Manual, Table B-1):

- Identify all control technologies (including lowest achievable emission rate or LAER)

- Eliminate technically infeasible options

- Rank remaining control technologies by control effectiveness

- Evaluate the most effective control and document results

- Select BACT

In brief, the top-down process requires all available control technologies to be ranked in descending order of effectiveness.  The PSD applicant first examines the most stringent – or “top” – alternative.  That alternative is established as BACT unless the applicant demonstrates, and the permitting authority in its informed judgment agrees, that technical considerations, or energy, environmental, or economic impacts justify a conclusion that the most stringent technology is not “achievable” in that case.  (NSR Manual at p. B.2.)

The PDOC does not contain a responsive BACT analysis.  Instead, the PDOC has leapt to step 5, selecting “BACT 1" for gas turbines (PDOC, pp.7-8), without conducting the analyses required for any of the preceding steps. Two new technologies have been introduced into the marketplace, SCONOx and XONON. SCONOx has been  demonstrated in practice and approved by the US EPA. Had the District performed a formal top-down analysis, it would have included these two new technologies which are technically feasible and achieve lower emissions limits than those proposed for the CCPP. This, as any other environmental analysis performed by the District and CEC, requires compliance with the California Environmental Quality Act (CEQA) and the National Environmental Policy Act (NEPA) requirements to examine alternative control technologies. The District has failed to identify BACT by failing to perform a top-down BACT analysis.

# BACT HAS NOT BEEN REQUIRED FOR NOx

The PDOC concludes that BACT for nitrogen oxides ("NOx") is an emission limit of 2.5 ppm at 15% O2 averaged over 1 hour, achieved using dry low NOx combustors ("DLN") and selective catalytic reduction ("SCR") technology, during all conditions except startups and shutdowns. Ammonia slip was separately limited to no more than 10 ppm (PDOC pp.5).  The Applicant and the District have made this determination without proper evaluation of two alternative control technologies, SCONOx and XONON.  As described below, BACT for NOx is an emission limit of no more than 1.3 ppm at 15% O2 averaged over 1 hour and no ammonia slip, which can be achieved by using SCONOx and other technologies.

## SCONOx Should Have Been Considered In A Top-Down BACT Analysis

SCONOx is a catalytic system that simultaneously oxidizes carbon monoxide ("CO") to carbon dioxide ("CO2"), hydrocarbons to CO2 plus water ("H2O"), and nitrogen oxide ("NO") to nitrogen dioxide ("NO2"). The NO2 is then absorbed onto a potassium carbonate-impregnated ceramic-based catalyst.  Passing a dilute hydrogen reducing gas across the surface of the catalyst in the absence of oxygen continuously regenerates the catalyst.  The hydrogen reacts with nitrites and nitrates to form water and elemental nitrogen.  Carbon dioxide in the regeneration gas reacts with potassium salts to form potassium carbonate, which is the absorber coating that was on the surface of the catalyst before the oxidation/absorption cycle began.

There is no indication in the PDOC (except for PDOC pp.8) that any technology other than SCR was considered.  This by itself is a clear violation of the PSD rules.  The first step of the top-down process is to identify all available control options.  (NSR Manual, pp. B.5, B.10-B.11, Table B-1.)  SCONOx is clearly among the technologies available.  EPA has stated, “SCONOx (and possibly in the near future XONON) should be included in a BACT/LAER analysis for proposed combined cycle gas turbine power plant projects in Region 9.”  (Haber 3/24/00.)  Furthermore, the South Coast Air Quality Management District (“SCAQMD”) has concluded that SCONOx achieves the Lowest Achievable Emission Rate (“LAER”) for NOx.  (SCAQMD 5/98).   Technologies that satisfy LAER “must also be included as control alternatives [for BACT purposes] and usually represent the top alternative.”  (NSR Manual, p. B.5.)  Therefore, SCONOx must be included in the District’s BACT analysis.

A proper top-down analysis would almost certainly conclude that SCONOx is BACT for this project, even if it achieved exactly the same emission limit as SCR, because it offers a number of important advantages over SCR alone, with no offsetting disadvantages.  First, SCONOx uses a single catalyst to simultaneously remove NOx, CO, VOCs, and toxics.  Second, it uses no ammonia or other hazardous materials and thus requires no ammonia slip, eliminating the many significant impacts associated with ammonia use (e.g., transportation accidents, unloading accidents, site releases, PM10 generation).  Third, the SCONOx system operates effectively at temperatures ranging from 300oF to 700oF, making it well suited for merchant operation and providing better control during startups and shutdowns than achieved with other competing catalytic technology (e.g., SCR, CO oxidation catalyst).  Fourth, unlike other catalytic systems, the SCONOx catalyst is continuously regenerated, assuring continuous maximum catalyst effectiveness.  Finally, notwithstanding the forgoing benefits, SCONOx has achieved much lower NOx and CO levels than other competing technologies and, therefore, is de facto BACT for this project.

There is no indication in the PDOC that SCONOx was properly considered.  The District appears simply to have adopted the Applicant’s choice of SCR without any scrutiny or appropriate alternative analysis pursuant to CEQA and NEPA of any kind, relying only on its outdated guidelines and applicant provided data.  The District's guidelines are no substitute for a formal top-down BACT analysis.  Further, if SCONOx was in fact considered and rejected in favor of a less beneficial technology such as SCR, then the District must clearly justify its choice in the public view.  (See In re Columbia Gulf Transmission Co., 2 E.A.D. 824, 827 (Adm’r 1989) (detailed substantiation required when rejecting most effective technology).)

The District, as EPA’s delegate, has an affirmative duty under the Clean Air Act to promote the use of more environmentally protective technologies.  (74 U.S.C. §§ 7475(a)(4), 7479(3).)  Thus, the District should have either required that the Applicant perform a proper BACT analysis, or conducted the analysis itself, since a permit decision must reflect a level of detail and analysis indicating that the permit issuer has reached a considered judgment.  (In re: Knauf Fiber Glass, GmbH, PSD Appeal Nos. 98-3 through 98-20, slip op. at p. 15 (EAB, Feb. 4, 1999); In re Pennsauken Co., N.J., Resource Recovery Facility, 2 E.A.D. 662, 667 (Adm’r 1988); In re Ash Grove Cement Co., RCRA Appeal Nos. 96-4 & 96-5, slip op. at 41 (EAB, Nov. 14, 1997); In re Austin Powder Co., 6 E.A.D. 713, 720 (EAB 1997); In re Gennesee Power Station, L.P., 4 E.A.D. 832, 835 (EAB 1993); In re Pennsauken Co., N.J., Resource Recovery Facility, 2 E.A.D. 667, 672 (Adm’r 1988) (remanding a PSD permit because the record did not contain the level of detail and analysis required).)

As discussed below, SCONOx is BACT for NOx for this project under PSD regulations because it achieves the "maximum degree of reduction" for NOx and is additionally commercially available, technically feasible, environmentally superior, and cost effective.  It has significant environmental advantages compared to its nearest competitor, SCR, because it eliminates the risks of handling ammonia and degradation of air quality from the generation of PM10.  In the following sections, CARE first presents the evidence that SCONOx has been demonstrated to achieve a lower NOx limit than any other technology.  CVRP then discuss the evidence that SCONOx is commercially available, technically feasible, cost-effective, and environmentally superior.

## NOx Emission Limit Of 2.5 ppmv Is Not BACT

The District concluded that BACT for NOx is an emission limit of 2.5 ppmv @ 15% O2 averaged over 1 hour.  Lower NOx levels have been required in permits and achieved in practice.  These lower levels should have been included in the District's BACT analysis.  The PDOC contains no evidence that the District considered any other emission limit.  The NSR Manual requires that "the most effective control option not eliminated in step 4 is selected as BACT."  (NSR Manual, p. B.53.)  In this section, CARE demonstrate that a lower NOx limit than proposed by the District, 1.3 ppm, has been achieved in practice.  In the next section, CARE demonstrates that there is no ground for eliminating the technology, SCONOx that has achieved this lower limit.

In 1998, the U.S. EPA concluded, based on six months of Continuous Emission Monitoring (“CEM”) data, that the Federal Facility had “demonstrated in practice” NOx emissions rates that are consistently at or below 2.0 ppmvd based on a 3-hour rolling average.  (Haber  3/23/98.)  The South Coast Air Quality Management District (“SCAQMD”) subsequently independently concluded based on this same data that the Lowest Achievable Emission Rate (“LAER”) for NOx for gas turbines greater than 3 MW in rated capacity is 2 ppm based on a 3-hour average or 2.5 ppm based on a 1-hour average.  (SCAQMD 6/12/98.)  LAER emission limits are the top alternative in a BACT analysis and must be adopted as BACT unless eliminated based on economic or environmental factors.  (NSR Manual, p. B.5.)  An emission limit of 2.5 ppm averaged over 1 hour has been adopted as BACT for all large gas turbines permitted in California since, based on EPA’s and the SCAQMD’s determinations for the Federal Facility (e.g., Sutter Power Project, High Desert Power Project, La Paloma Generating Project, Los Medanos Energy Center, Delta Energy Center).

### Federal CEMs Data Indicates BACT Is 1.3 ppm NOx

The Applicant will argue that SCONOx does not offer any improved performance with respect to NOx control, compared with SCR and the "unappealing characteristics of SCONOx are not offset by any significant improvement in overall NOx emission reduction performance."  However, the most recent CEMs operating data from the Federal Facility demonstrate that they are wrong.  Further, the vendors are willing to guarantee NOx emission limits of 1 ppm averaged over 1 hour.  This is clear evidence of improved performance compared to SCR.

Since EPA and the SCAQMD made their BACT determinations based on the Federal Facility in 1998, the performance of the SCONOx unit at the Federal Facility has been improved by adding more catalyst so that it now consistently meets a lower NOx emission limit.  Further, it has been converted from a base load facility to a merchant facility, which means that it is more representative of the Contra Costa Power Project.

Other parties collected 9 months of CEMs data from the Federal Facility for the period April 1, 1999 through December 31, 1999 and analyzed it to establish the “maximum degree of reduction” or BACT for both NOx and CO. the continuous emission monitors at the Federal Facility are certified annually by the SCAQMD.  In addition, Sunlaw conducts annual stratification source tests to verify that the location of the CEMs sampling point in the stack is representative of the average exhaust gas concentration.  The results of the stratification test conducted during this 9 month period shows that the CEMs sampling location was within 0.07 ppm or 8.1% of the measured average concentration.

It is important to note that this data is from the very same facility that was used by both the EPA and the SCAQMD to establish the 2.5-ppm BACT level that has been widely permitted in California and accepted by the District for other large combined cycle merchant plants.  Thus, there can be no dispute that additional data from this same facility is relevant to this Project and is a reasonable basis to establish a lower BACT NOx level.

The 1-hour average NOx CEMs data for the modified Federal Facility are summarized in (05-31-00) CVRP’s comments on the CCPP PDOC, Figure 1.  This figure excludes excursions due to startup, shutdown, and non-SCONOx operating problems (e.g., CEM failure, plant trips, operator error, condensation in gas generator), as allowed by the permit.  Rolling averages were calculated from 15-minute data in the file in by eliminating all valid exceedances based on the operating log and averaging the remaining data in groups of four 15-minute segments.  All such excursions are documented based on the plant-operating log.

The maximum reported NOx concentration is 1.275 ppm as a 1-hour rolling average, and 1.254 ppm as a 3-hour rolling average.  Figure 1 is based on 9,380 15-minute average NOx measurements out of a total possible of 25,595 because the plant was operated in merchant mode and only dispatched about 37% of the time due to mild weather conditions in 1999.  These data demonstrate that BACT for NOx should be established at 1.3 ppm averaged over 1 hour.

### Other Data Confirm That BACT For NOx Is Lower Than 2.5 ppm Averaged Over 1 Hour

Other information also confirms that BACT for NOx is lower than 2.5 ppm averaged over 1 hour required for this Project.

First, SCONOx has been installed on a second power plant, at the Genetics Institute in Andover, Massachusetts, which is reportedly meeting a 1-ppm NOx limit when the turbine is functioning properly.

Second, both Massachusetts and Connecticut have made BACT determinations and issued permits requiring that large gas turbines achieve a NOx limit of 2 ppmv at 15% O2 averaged over 1 hour.  These permits are based on clock or block averages, identical to the averaging time proposed for Metcalf.  This is a lower emission limit than 2.5 ppmv averaged over 1 hour.

Notwithstanding the CEMs data reviewed above, these permits alone establish a lower NOx emission limit for Contra Costa Power Plant than that required in the PDOC and therefore should have been considered by the District.  The lowest permit limit required in any construction permit which has been issued anywhere in the country in the time period up to and including the public comment period on a permit establishes BACT. Hence, even if the CEMS data from the Federal Facility did not establish a new BACT level for this Project (which it does), the BACT determinations made in Massachusetts and Connecticut, which specify a NOx limit of 2 ppmv averaged over 1 hour, would constitute a new BACT level for this Project.  Thus, the District must include 1.3 ppm NOx in its BACT analysis.

### NOx Levels Of 1 ppm Can Be Accurately Measured

In other forums, it has been argued that the NOx BACT limit should not be lowered because NOx cannot be accurately measured, even at 2.5 ppm.  (CARB 9/99, pp. 24-25.)  These and similar issues were also raised in the South Coast AQMD’s proceedings in which the 2.5 ppmvd BACT level was originally adopted.  The South Coast AQMD thoroughly evaluated and rejected all of these measurement issues as insignificant in its staff report (South Coast AQMD Staff Report) and in correspondence. (Gangule 5/26/98.)

NOx levels can be accurately measured at 1.0 ppm.  This has been demonstrated at the Sunlaw Federal Facility, where three separate monitoring systems were used there to measure NOx:  (1) the facility CEM, which is an API Series 200 CEM with a lower limit of detection and precision of 0.1 ppm; (2) South Coast AQMD Reference Method 100.1 by South Coast AQMD staff; and (3) in annual certification tests by an independent source testing firm using the RECLAIM Rule 2012 protocol.  All three testing methods provided consistent measurement results.

Manufacturers of NOx CEMs -- Rosemount Analytical, California Analytical Instruments, Thermo Analytical Instruments, and Advanced Pollution Instruments -- all offer CEMs that are guaranteed to measure NOx from 0 to 10 ppm with a lower limit of detection of 0.1 ppmv NOx or 1% of full scale, and a precision of the greater of either 0.1 ppm or 1% of full scale or better.  This is well below the BACT level of 1.3 ppm and is consistent with the results of certification and inter-method comparison studies at the Sunlaw Federal Facility, and provides a comfortable margin of safety.  Thus, CARE contends that measurement issues should not limit the establishment of BACT for gas turbines at 1.3 ppm.

## SCONOx Is Technically Feasible Under PSD Regulations

The top-down BACT analysis process allows a control option to be eliminated if it is technically infeasible or results in adverse energy, environmental, or economic impacts.  (NSR Manual, § B.)  The NSR Manual clarifies when a technology is technically feasible:  “[I] f the control technology has been installed and operated successfully on the type of source under review, it is demonstrated and it is technically feasible.”  (NSR Manual, p. B.17.)  SCONOx meets this test, as demonstrated below.

### SCONOx Has Been Installed And Successfully Operated

The SCONOx system has been demonstrated to achieve 2 ppmvd averaged over 3 hrs or 2.5 ppmvd averaged over 1 hr on the 32 MW combined cycle (25 MW LM2500 gas turbine plus 7 MW steam turbine) Federal Cogeneration facility in Vernon, California (“Federal Facility”).  (South Coast AQMD Staff Report, p. 3-4.)  The South Coast AQMD has concluded that SCONOx/water injection is “achieved-in-practice” technology for natural gas-fired turbines with rated capacities of 3 MW or greater.  EPA Region 9 has also concluded that the Federal Facility “has, based on data submitted to EPA for the six-month period from June 28, 1997 to December 28, 1997, ‘demonstrated in practice’ NOx emissions rates that are consistently at or below 2.0 ppmvd based on a 3-hour rolling average.”  (Haber 3/23/98.)  EPA has recently acknowledged that this same facility is currently meeting 1 ppm NOx. In addition, SCONOx has been operating on a 5-MW Solar Taurus 60 gas turbine at the Genetics Institute facility in Andover, Massachusetts since August 1999, likewise meeting 1 ppm.

Setting aside the more stringent technical feasibility demonstration discussed above, which SCONOx meets, the NSR Manual alternatively defines a technology as technically feasible if it is both “available” and “applicable.”  (NSR Manual, p. B.17.)  A technology is considered “available” “if it has reached the licensing and commercial sales stage of development.”  (Ibid, p. B.18.)

### SCONOx Is Available

The Applicants have argued that SCONOx is not BACT because Massachusetts concluded in July 30, 1999, "the Department cannot conclude that SCONOx is the Best Available Control Technology for the control of NOx for turbines larger than 50 megawatts."  (MEC Response to CVRP Data Request 7a, p. 6.)  When this was written, ABB had not completed its evaluation and scale up program and was not commercially offering SCONOx.  However, ABB Alstom Power announced on December 1, 1999 that SCONOx is commercially available for large gas-fired turbines.  ABB Alstom Power has licensed SCONOx from Goal Line and is the exclusive licensee for power plants larger than 100 MW. Goal Line representative Gary Gifford will act as CARE’s expert witness in this matter or this case.  Goal Line itself may sell the SCONOx system if ABB cannot or will not sell SCONOx to a given applicant.  ABB Alstom Power has completed testing and scale-up of the technology and is now offering it for sale with performance guarantees, specifically targeting the largest gas turbines made (e.g., ABB GT-24, Westinghouse 501G) or announced (e.g., GE Frame 7H).  The technology is fully described on ABB's website. (www.apcnoxcontrol.com.)

The ABB announcement was based on the completion of scale-up testing by ABB, which was subsequently reviewed and confirmed by Stone & Webster.  This work included a comprehensive review and analysis of design documents for a 270 MW reference plant consisting of one ABB GT-24 turbine, one HRSG, and one steam turbine.  A full-scale prototype damper system for this plant was constructed and operated on a test rig for 101,000 cycles, equivalent to about 5 years of continuous operation.  Regeneration gas flow distribution through the catalyst was investigated using both computer and physical model studies.  A control system failure mode analysis was also performed.

In addition, Marsh USA Inc. conducted an insurance review and concluded that "CVRP did not discover any issues that cannot be readily addressed by ABB or which, in our opinion, make the SCONOx system uninsurable."  They further concluded, "The underwriting community will positively embrace SCONOx as a viable product that reduces industry emissions.  Realistically, due to the method in which pricing is determined, CVRP expect no additional premium credit being applied to project insurance if a SCONOx system is installed."  (Marsh 10/6/99.)

### SCONOx Is Applicable

The NSR Manual additionally considers a technology to be “applicable” “if it has been or is soon to be deployed (e.g., is specified in a permit) on the same or a similar source type.”  (Ibid. p. B.18.)  The San Joaquin Valley Air Pollution Control District has specified SCONOx in a permit on a 262-MW ABB GT-24 gas turbine issued to the La Paloma Generating Co. LLC in an authority to construct permit issued May 26, 1999, by the San Joaquin Valley AQMD.)  It has also been proposed for use on the 510-MW Otay Mesa Project at 2 ppm with a goal of 1 ppm, and on the 550-MW Nueva Azalea Project at 1 ppm NOx and 0.5 ppm CO.  Therefore, even if SCONOx had not been installed and successfully operated on two gas turbines representing the same “type” of source, it would still be judged to be technically feasible using EPA’s alternate criterion for situations where there is no actual operating experience.

### EPA Has Concluded SCONOx Is Technically Feasible

Finally, the U.S. EPA has determined that SCONOx is technically feasible.  EPA Region 1 recently concluded, based on correspondence with ABB Alstom Power, that “it is our view that SCONOx is a technically feasible control option for large combined cycle turbine project” and “the Region now considers SCONOx a technically feasible and commercially available air pollution control technology that is expected to obtain emission levels for criteria pollutants such as NOx, CO and VOC comparable or superior to previously applied technologies for large combined cycle turbine applications.”  The EPA and ABB correspondence supporting this conclusion are included in (5-31-00 CVRP comments on CCPP PDOC, Ex. 16: Region I letter).

### There Is No Demonstration Of Technical Infeasibility

The NSR Manual notes “the control option is presumed to be technically feasible unless the source can present information to the contrary.”  (NSR Manual, p. B.19.)  The demonstration of technical infeasibility must be “based on a technical assessment considering physical, chemical and engineering principles, and/or empirical data showing that the technology would not work on the emission unit under review, or that unresolvable technical difficulties would preclude the successful deployment of the technique.”  (Id., p. B.20.)   No such demonstration has been made in this case.

#### SCONOx Is Cost Effective

The Applicants argue that the installed capital cost of SCONOx is three to four times higher and the operating costs two to three times higher than a conventional SCR system.  This is irrelevant and incorrect.

First, it is simply irrelevant whether one technology which achieves much higher emission reductions (SCONOx) costs more than another with lower emission reductions.  The key question is whether the more expensive technology is cost-effective, regardless of how much more it may cost than a cheaper and less effective technology.  Cost effectiveness is an economic criterion used to assess the potential for achieving a control objective at the lowest cost.  Cost is measured in terms of annualized control costs, and effectiveness is measured in terms of tons of pollutants removed per year.  Therefore, cost effectiveness is the total annualized costs of control divided by annual emission reductions.  (NSR Manual, p. B.36.)  The EPA has developed guidelines for determining cost-effectiveness (NSR Manual, § IV.D.2.b) and procedures to perform the requisite calculations.  (OAQPS Manual.)

Second, vendor cost data indicates that while installed capital costs for SCONOx are about twice as high as an SCR/oxidation catalyst, the annual operating costs for SCONOx are lower than the conventional system.  The overall cost effectiveness of SCONOx well within BAAQMD and other agency guidelines.

Specifically, recent independent cost-effectiveness analyses based on EPA guidelines and procedures indicate that SCONOx costs $6,270 per ton of NOx (“$/ton”) to reduce NOx from 25 ppm to 2 ppm on a GE Frame 7 machine.  (OnSite Sycom 10/15/99, Table A-7.)  Cost estimates prepared by CURE for Elk Hills indicate that SCONOx costs $7,360/ton to reduce NOx from 9 ppm to 2.5 ppm on a GE Frame 7 machine.

We prepared a cost effectiveness analysis for the Contra Costa Power Project that assumes BACT emission limits of 2.5 ppm NOx and 6 ppm CO.  Our calculations, summarized in Table 1, are based on vendor-supplied costs and emissions from the PDOC, assuming inlet concentrations of 25 ppm NOx and 10-ppm CO.  (PDOC, pp. A-2 to A-3.)  Our calculations give no credit for emission reductions during startup, and thus overstate the cost per ton of emissions reductions using SCONOx. Nevertheless, these calculations indicate that SCONOx costs between $5,651 and $6,028 per ton of NOx removed.  The cost effectiveness drops to $4,601 to $5,440 per ton when both nonattainment pollutants are included in the calculation.  This is reasonable here and has been requested by EPA for other facilities because SCONOx controls both pollutants simultaneously.

All of the SCONOx costs discussed above, ranging from $4,601per ton of CO or NOx to $7,360 per ton of NOx alone, are well within the BAAQMD’s cost-effectiveness criterion.

In the Bay Area Air Quality Management District, the maximum cost per ton of NOx controlled that is considered cost-effective is $17,500.Therefore, SCONOx is cost-effective.

# D. OTHER BENEFITS OF SCONOx NEED TO BE CONSIDERED IN DETERMINING BACT

The SCR system proposed for use by the Applicants results in a number of environmental problems that are reduced or eliminated with the use of SCONOx.  These problems include: (1) hazards from accidental releases of the ammonia used in the SCR system during its transportation and handling; (2) the formation of particulate matter from the oxidation of SO2 in the SCR catalyst; (3) the formation of particulate matter from reactions between ammonia and SO2;  (4) generation and disposal of the hazardous SCR catalyst at the end of its useful life; (5) inability to control NOx and CO emissions during startups and shutdowns; (6) increase in NO2 from the use of dry low NOx combustor.

SCONOx and SCR are compared in Table 2.  SCONOx offers a number of important advantages over a conventional SCR, with no known disadvantages.  First, SCONOx uses a single catalyst to simultaneously remove NOx, CO, and VOCs.  A conventional system requires two separate catalyst systems.  Second, SCONOx uses no ammonia or other hazardous materials and thus requires no ammonia slip, eliminating the many significant impacts associated with ammonia use (e.g., transportation accidents, unloading accidents, accidental releases of ammonia, PM10 generation).  Third, the SCONOx system operates effectively at temperatures ranging from 300oF to 700oF, making it well suited for merchant power plant operation and providing better control during startups, shutdowns, and load swings than achieved with other competing catalytic technology.  Fourth, unlike other catalytic systems, the SCONOx catalyst is continuously regenerated, assuring continuous maximum catalyst effectiveness.  The performance of a conventional catalyst system, on the other hand, degrades with use.  Fifth, SCONOx has been demonstrated to  achieve much lower NOx and CO levels than other competing technologies, at lower overall costs.  Finally, the SCONOx catalyst contains precious metals, which can be reclaimed by smelting, reducing overall operating costs.  The SCR catalyst must be disposed as a hazardous waste at the end of its useful life.  The ammonia impacts and startup/shutdown emissions are discussed further below.

## 1. SCONOx Eliminates Ammonia Impacts

The District selected SCR with an ammonia slip of 10 ppm as BACT for NOx without performing a proper environmental analysis as required by the top-down BACT process.  (See NSR Manual at B.6.)  PM10 is formed from two sources in an SCR system -- ammonia slip and oxidation of SO2 to sulfur trioxide (SO3) by the SCR catalyst.  Ammonia and sulfur trioxide form particulate matter within the stack and secondary PM10 downwind in the atmosphere.  This PM10 can cause health impacts, visibility impairment impacts, contribute to existing exceedances of the California ambient PM10 standard, and impact listed and protected species.  These collateral increases in PM10 have not been evaluated.  Further, ammonia is a hazardous substance, and the transportation and handling of ammonia can result in accidental releases that adversely impact the public.

### 2. Ammonia Impacts Must Be Considered

The top-down BACT process and the federal law it implements require that the environmental impacts of selected technologies be considered as part of the BACT determination.  The federal Clean Air Act defines BACT as an “emission limitation” that is set “on a case-by-case basis . . . taking into account energy, environmental, and economic impacts and other costs.”  (42 USC § 7479(3), (emphasis added).)  The Environmental Appeals Board has provided the following interpretation of the emphasized portion:

[I]f application of a control system results directly in the release (or removal) of pollutants that are not currently regulated under the Act, the net environmental impact of such emissions is eligible for consideration in making the BACT determination.  [As a result of the analysis], the control system proposed as BACT may have to be modified or be rejected in favor of another system.  In other words, EPA may ultimately choose more stringent emission limitations for a regulated pollutant than it would otherwise have chosen if setting such limitations would have the incidental benefit of restricting a hazardous but, as yet, unregulated pollutant.  (North County Resource Recovery Associates, 2 E.A.D. 230 (EAB 1986).)

The U.S. EPA has similarly interpreted this requirement to mean that, where two technology choices provide equivalent control for a regulated pollutant, but one would also control pollutants not directly regulated by the PSD Program, such as PM10 and NH3 in this case, the one controlling the unregulated pollutants should be chosen as BACT.  Moreover, EPA is seeking to integrate pollution prevention as an ethic throughout its activities.  (Habicht 5/28/92.)

The NSR Manual itself is clear that the environmental analysis should also include a consideration of “...visibility impacts, or emissions of unregulated pollutants.”  (NSR Manual, p. B.46.)   Thus, even if SCONOx did not achieve lower NOx limits than other technologies, SCONOx should have been deemed BACT on the basis that it eliminates ammonia emissions.

### a. PM10 Formation From Oxidation Of SO2 And Ammonia Slip

The SCR catalyst oxidizes SO2 to SO3.  The excess residual ammonia downstream of the SCR system (i.e., the slip) reacts with this SO3 as well as NO2 and water vapor in the stack gases and downwind in the atmosphere to form ammonium sulfate, ammonium bisulfate, and ammonium nitrate according to the following reactions.  (Seinfeld and Pandis 1998, pp. 529-534; South Coast AQMD 6/12/98, p. 3-3; Matsuda et al. 1982; Burke and Johnson 1982.)

SO3 + 2 NH3  (NH4)2SO4	 			(1)

SO3 + NH3  NH4HSO4				(2)

NO2 + OH + NH3  NH4NO3			(3)

- The resulting salts form particulate matter, which contributes to ambient PM10, causes maintenance problems in the HRSG, contributes to visibility impairment, and impacts protected species.   These salts cause a number of environmental problems, which are addressed below.

#### i. PM10 Formation Contributes To Existing Violations Of State Standards

- The reactions between SO3, NH3, and NO2 form salts, some of which are emitted to the atmosphere and some of which deposit within the HRSG.  The above equations can be used to estimate a portion of the secondary PM10 that is formed from ammonia slip.  Secondary PM10 can be formed by reaction of ammonia with SO3 and NO2 emitted by the gas turbines and present in the stack gases and plume as well as additional SO3 and NO2 that are present downwind in the atmosphere.

- CVRP calculated the amount of secondary PM10 that could form from the reaction of ammonia slip with NO2 and SO3 in the turbine exhaust.  The calculations in Table 3 show that Equation (1) would produce up to 3.9 ton/yr of ammonium sulfate secondary PM10 from reaction of ammonia only with combustion byproducts.  Additional ammonium sulfate would form from reaction of SO3 in the atmosphere with any emitted ammonia.  Table 4 shows that Equation (3) would produce up to 105.8 ton/yr of ammonium nitrate secondary PM10 from reaction of ammonia only with combustion byproducts.  Some this PM10 would be deposited within the HRSG and the balance emitted.  Additional ammonium nitrate could form from the reaction of NO2 in the atmosphere with any emitted ammonia.  This additional PM10 was not included in the Project’s emissions estimates.

#### ii. PM10 Formation Causes SCR Maintenance Problems

- Some of these salts estimated in Tables 3 and 4 deposits in the low-pressure tube sections of the HRSG.  According to GE, "[a]ctual operating experience indicates that ammonium-sulfur salt formation and boiler damage occur without exception, when ANY sulfur bearing fuel is fired in the gas turbine and SCR is used for NOx control.  This is not usually accounted for in BACT determinations, but adds significant cost, and should be considered." These salts build up, decreasing heat transfer and increasing operating costs.  They also corrode the boiler tubes, requiring periodic cleaning and periodic replacement of the low-pressure tube sections of the HSRG.  (Id., pp. 1, 3.)  This affects the reliability and maintenance costs of SCR and thus must be considered in the BACT analysis.  The salt deposition problem will be aggravated by the use of dry low NOx combustors, which increase the amount of NO2 in turbine exhaust gases, and hence the amount of ammonium nitrate that may form in the HRSG.  (ASME 1/1/99.)

#### iii. PM10 Formation Causes Visibility Reduction

- The fact that these reactions actually occur and cause visibility impacts is well documented in the technical literature.  A noted atmospheric textbook, for example, contains this vivid description of the problem (Pitts and Pitts, 1999,  p. 284):

- "The formation of ammonium nitrate has some interesting implications for visibility reduction.  In the Los Angeles air basin, for example, the major NOx sources are at the western, upwind end of the air basin.  Approximately 40 miles east in the vicinity of the city of Chino, there is a large agricultural areas that has significant emissions of ammonia...under typical meteorological conditions, air is carried inland during the day, with NOx being oxidized to HNO3 as the air mass

- moves downwind.  When it reaches the agricultural area, the HNO3 reacts with gaseous NH3 to form ammonium nitrate, the particles formed by such gas-to-particle conversion processes are in the size range where they scatter light efficiently, giving the appearance of a very hazy or smoggy atmosphere even though other manifestations of smog such as ozone levels may not be highly elevated."

# E. ALTERNATIVES TO SCONOx TO ACHIEVE A NOx BACT of 1.3 ppm

- There are alternatives to SCONOx that achieve 1.3 ppm NOx averaged over 1 hour with very low ammonia slip.  A standard SCR can be designed to achieve a NOx level of 1 ppm, comparable to SCONOx, by simply adding more catalyst and increasing the catalyst change out efficiency.  The ammonia slip can be reduced or eliminated by using this standard system by either designing the SCR to achieve a lower ammonia slip and by following the SCR with a CatCO oxidation catalyst to remove ammonia.   These two options are discussed below.

## 1. Standard SCR Designed For A Lower NH3 Slip

- Lower slip levels can be readily and inexpensively achieved using a standard SCR system designed to meet a lower slip.  The CARB Guidance Document recommends a slip of less than 5 ppm and acknowledges that slips as low as 2 ppm can be achieved using standard technology.  (CARB 9/99,  pp. 25-26.)

- Very low slips have been achieved in practice at large natural gas-fired turbines that comply with vendor-recommended maintenance (e.g., annual catalyst washing.)  The Hitachi NOx guarantee letter in Appendix D of the CARB Guidance Document, for example, identifies a 1400-MW plant consisting of four GE Frame 9 gas turbines that is currently operating at a NOx level of 3 ppmvd with a 3-ppmvd ammonia slip in Japan.

- Both Massachusetts and Rhode Island have established 2-ppm ammonia slip BACT limits for new power plants.  Rhode Island requires all power plant permit applicants to justify why they cannot achieve a 2ppm ammonia slip for SCR as part of their BACT analysis.  The Massachusetts Department of the Environmental Protection ("MDEP") has established a “Zero Ammonia Technology” BACT standard for gas turbines larger than 50 MW.  (Struhs 1/29/99.)

- Three large projects in the Massachusetts market, the 350-MW Cabot Power Island End Project, the 420-MW American National Power Blackstone Project, and 1,550-MW Sithe Mystic Development have been issued PSD permits specifying a NOx limit of 2 ppm achieved with a 2 ppm ammonia slip, demonstrated using an ammonia CEMs and both averaged over 1 hour.  Their permits further require that they retrofit with zero ammonia technology at the end of five years.

- All of the major SCR vendors will guarantee ammonia slips substantially below 10 ppm.  Attachment D to the CARB Guidance Document includes performance guarantees from four of the major SCR vendors for a 5-ppmv slip, the only level requested.  A slip level of 5 ppm is currently proposed for the recently approved Moss Landing Project.  The CEC staff has preliminarily called for a 5-ppmv ammonia slip limit for CCPP. In addition, all of the major vendors are currently offering performance guarantees of 2 ppmvd to compete in the New England market.

- Finally, the CARB Guidance Document recommends “that districts consider establishing ammonia slip levels below 5 ppmvd at 15 percent oxygen in light of the fact that control equipment vendors have openly guaranteed single-digit levels for ammonia slip.”  (CARB 9/99, p. 26.)

# BACT HAS BEEN REQUIRED FOR CO – LOWER CO LEVELS HAVE BEEN ACHIEVED

The District's BACT Guideline 89.2.1 establishes a BACT limit of < 6 ppm or 90% CO reduction as technologically feasible and cost effective and 10 ppm as achieved in practice, both achieved with an oxidation catalyst.  U.S. EPA guidance, only requires that a limit be specified in a permit to be selected as the top technology in the top-down BACT process.  Other recently permitted projects in California, outside of the District, have been permitted at 6 ppm (e.g., La Paloma, Sunrise, Elk Hills).  Further, other states have required much lower CO limits (2 ppmv averaged over 1 hour) in recently issued PSD permits.  These lower limits, which have been established in valid PSD permits, should have been included in a proper top-down BACT analysis.  There is no obligation under federal law to constrain a BACT determination to the boundaries of the permitting agency, as done here.  BACT knows no boundaries, and, in fact, EPA acknowledges foreign experience as relevant.

The specifics (e.g., duct burners, steam injection, merchant mode) of the Contra Costa Power Project do not affect the performance of catalytic systems.  In these processes, simply adding more catalyst to reduce space velocities can increase removal efficiencies.  Therefore, even if duct burners and steam injection for power augmentation appreciably increased CO levels, which they apparently do not, it would not affect the performance of a properly designed catalytic process.  The increase in CO, if any, could be removed by simply designing the system to include the proper amount of catalyst require to achieve the target emission limit.

Under the PSD program, BACT is “an emissions limitation . . . based on the maximum degree of reduction for each pollutant subject to regulation under [the] Act which would be emitted from any proposed major stationary source . . . .” (40 CFR § 52.21(b)(12), emphasis added.)  The information reviewed below indicates that 0.5-ppm CO averaged over 3 hours is achieved in practice.  Therefore, the District has failed to specify BACT for this Project.

### A. Crockett Experience Is Irrelevant

- The Crockett facility has been unable to meet its 5.9-ppm CO limit during minimum load under ambient conditions of low temperature and high relative humidity and during peak load under ambient conditions of high temperature and moderate to high relative humidity.

- However, the gas turbine at Crockett is recognized by CARB “as being somewhat unique, since it is an early version of the General Electric Frame 7FA” which has since been discontinued.  The rotor was recently replaced due to vibration and blade erosion problems.  The combustor has also been replaced, with subsequent CO emissions below 10 ppmv.  In CARB’s opinion, the compliance problems at Crockett “appear to be related specifically to this gas turbine or overall system and not necessarily to the oxidation catalyst.”  CARB specifically cautioned that this experience is unique and should not be applied to other projects, as advocated here by the District.  (Menebroker 9/1/99.)

- Further, Engelhard, the vendor of the oxidation catalyst, has conducted extensive investigations into the possible causes of the CO compliance problems at Crockett.  Contrary to the District's claims, it has concluded that the compliance problems are unlikely to be related to either the weather or the catalyst itself (plug samples consistently showed the catalyst was good), a similar catalyst at the same site was operating properly, and numerous similar facilities are in successful operation worldwide.  (Mack 7/19/99.)  There are other, more plausible explanations, not related to the efficacy of the catalyst itself.  These include sugar deposits (from the adjacent C&H sugar plant), catalyst plugging from internal insulation sloughing, and turbine problems.  Therefore, the District has inappropriately used the Crockett experience to establish a CO BACT limit for Contra Costa Power that is higher than CO levels achieved in practice at other power plants.

### B. Source Tests Support A CO Limit <1 ppm

The information compiled in the CARB Guidance Document supports a much lower BACT level than 6 ppm averaged over 3 hours.  For combined-cycle plants, the most stringent emission limit for CO required in a construction permit is 1.8 ppmvd at 15%O2 averaged over 1 hour at the Newark Bay Cogeneration facility.  (CARB 9/99, Table C-6.)  Compliance with this limit was demonstrated in a source test.  (Id., Appx. C, p. 26.)  Moreover, the actual CO concentrations measured in all nine of the CO source tests summarized in the Guidance Document are at or below 2.0 ppmvd at 15% O2.  (Id., Table C-8.)  These data support a BACT level for CO for combined-cycle plants of 2.0 ppmvd @ 15% O2 averaged over 1 hour.

In addition, source test data for four additional combined cycle and cogeneration gas turbines equipped with oxidation catalysts (Table 5) support a CO BACT level of less than 1 ppm.  Table 5 includes six sets of source tests that were performed at loads ranging from 50% to 100%.  These partial load data are representative of merchant operation and indicate that CO (and VOC – see Table 5) levels during partial load operation are comparable to those during full load operation.  Most of the CO measurements, irrespective of load, are much less than 1 ppm.  These data confirm that BACT for CO for large combined cycle gas turbines in merchant operation is no more than 2.0 ppmvd @ 15% O2 averaged over 1 hour and support a BACT CO level of less than 1 ppm.

### C. SCONOx Achieves 0.7 ppm CO

SCONOx simultaneously removes NOx, CO, and VOCs.  The nine months of recent CEMs data discussed above in Comment III.B.1 indicate that the Federal Facility routinely achieves a CO limit of 1.0 ppm averaged over 1 hour, and 0.7 ppm averaged over 3 hours.  Similar performance has been demonstrated at the Genetics facility.  The 1-hour average CO data are summarized in Figure 2, and the 3-hour average data in Figure 3.  These figures exclude excursions due to startup, shutdown, and non-SCONOx operating problems (e.g., CEM failures, plant trips, operator error, condensation in gas generator).

Applicants have argued that duct firing would somehow limit SCONOx's ability to control CO.  This is erroneous.  SCONOx has been operating for nearly a year at the Genetics Institute in Andover, Massachusetts, which employs a duct-fired heat recovery steam generator (“HRSG”).  Because both the turbine and the duct burners burn natural gas, the emission characteristics are very similar.  In any event, the duct burner emissions comprise only a small fraction of the total exhaust gases, 7% in the case of Contra Costa Power Project that would have to be treated by a SCONOx system.  This small increase would not alter the system’s fundamental design.   Finally, the vendors of SCONOx have confirmed these facts and have further noted, based on experimental tests, that duct firing actually improves the performance of SCONOx, not reduces it as alleged by the Applicants.

The type of combustor is irrelevant to the performance of SCONOx.  The only important variable is inlet CO concentration.  ABB guarantees a CO reduction of 90%, irrespective of the inlet concentration.  Therefore, for CCPP, SCONOx could be designed to achieve 1.0 ppm CO.

### D. An Oxidation Catalyst Achieves 0.5 ppm

Continuous Emission Monitoring (“CEM”) data from the Southwest Air Pollution Control Agency (“SAPCA”) in Washington for the River Road Generating Project indicates that this facility, which is a large Frame 7, meets a CO limit of 0.5 ppm averaged over 3 hours.   The facility is a 248-MW natural gas fired, combined-cycle plant consisting of a GE 7231 FA gas turbine equipped with GE dry low-NOx combustors (DLN III), an unfired HRSG, and a steam turbine.  Control equipment includes an SCR system permitted at 4 ppmvd NOx at 15% O2 averaged over 24 hours, and a CO oxidation catalyst guaranteed by the vendor at 3 ppmvd at 15% O2 and permitted at 6.0 ppmvd at 15% O2 averaged over 3 hour.  The unit operates at loads from 75% to 100%, and experiences frequent shutdowns and startups.

The 1-hour averaged CEM data for the last four quarters of operation are included in (05-31-00 CVRP comments on MEC PDOC).  These data indicate that the River Road Generating Station routinely achieves a CO limit of 1.2 ppm averaged over 1 hour and 0.5 ppm averaged over 3 hours.  The 1-hour average data are shown in Figure 4 and the 3-hour average data in Figure 5.  All exceedances of these limits were due to startups, shutdowns, operator error, or equipment malfunctions reported to the SAPCA, with the exception of a single event on 12/20/98 from 12:00 PM to 1:00 PM.  Although not of a Westinghouse 501 F equipped with dry low NOx combustors can meet 6 ppm CO for all operating conditions proposed by CCPP.  Oxidation catalysts can be readily designed to remove 90% or more of the CO.  (Mack 7/19/99.)  Therefore, it is clearly feasible to meet a CO limit of 1.2 ppm averaged over 1 hour or 0.5 ppm averaged over 3 hours, consistent with the River Road data.

# OTHER AIR QUALITY Benefits Of CO control

The MEC Applicant's consultant argued that CO should not be controlled because stack concentrations are lower than ambient air quality standards and hence safe.  This argument turns the PSD program on its head by advocating for no CO control when an area is in non-attainment.  Further, the NSR Manual explicitly requires that the environmental tradeoffs of control technologies be evaluated.  In this case, the failure to control CO has the very real potential of increasing ozone, which would aggravate the Bay Area's existing ozone compliance problems.  Two significant benefits of controlling CO using SCONOx are discussed below.

## CO Control Simultaneously Removes VOCs, Which Are Ozone Precursors

The SCONOx catalyst consists of a ceramic substrate impregnated with platinum and is essentially the oxidation catalyst.  The SCONOx system achieves higher CO removal efficiencies because it operates at much lower space velocities, typically 22,000 per hour compared to 200,000 per hour for an oxidation catalyst.  Therefore, some collateral VOC (and toxics) reduction occurs across the catalyst, depending upon their operating temperatures, which are determined by their placement in the HSRG.

The collateral VOC (and toxics) reduction for a conventional CO catalyst could be as high as 50% of the quoted CO reduction, depending upon catalyst operating temperature and the composition of the exhaust gas stream.  (Heck and Farrauto 1995, Chapter 11.)  Aldehydes, alkanes, alkenes higher than butane, and aromatics, such as benzene, are readily oxidized across Engelhard's CO catalyst.  Most of the specific organic compounds found in turbine exhaust fall into these classes.  Reported removal efficiencies range from 71% for toluene to 86% for acetylene.  (Heck and Farrauto 1995, Table 11.1.)  Similarly, source tests at the Federal Facility, a low-temperature retrofit application, indicate that SCONOx reduces formaldehyde by 97% and acetaldehyde by 94%. (Delta 4/2/97; Delta 4/00.)

Generally, the higher the temperature, the higher the collateral VOC reduction.  For example, the vendor guaranteed a 30% non-methane, non-ethane hydrocarbon reduction and 80% CO reduction for the Tenaska 248 MW GE Frame 7FA combined cycle plant with the catalyst located in a high temperature zone of 1000 to 1100ºF.  The guarantee letter is attached in (the 05-31-00 CVRP comments on MEC PDOC).  Although we do not know the precise location and hence gas temperature where catalyst would be located in the Contra Costa Power Plant’s HRSG, it likely would be located in the high temperature zone of the HRSG where the temperature is 600-650 F.  Therefore, higher collateral VOC reductions as high as 80% and perhaps as high as 95% could be achieved for Contra Costa Power Plant using SCONOx.

## CO Itself Is An Ozone Precursor

- CARB and EPA Region 9 have historically declined to establish a lower CO BACT level than 6 ppm averaged over 3 hours because CO is in attainment in most of California, most of the ambient CO is caused by motor vehicles, and the current BACT level is less than the ambient air quality standard on CO (see CARB 9/99, p. 29).  However, these are not valid reasons under the federal definition of BACT to decline to establish a valid BACT limit.

Carbon monoxide is oxidized in the atmosphere to ozone.  Generally, the ozone formation potential of CO compared to most VOCs is quite low, but varies with atmospheric composition.  The ozone formation potential of CO is only 5% to 20% of that of poorly reactive alkanes (ethane, propane) and alcohols, and substantially less for more reactive compounds such as aromatics and highly reactive alkanes.  Because CO has a low ozone formation potential on a per weight basis, EPA and other regulatory agencies do not consider CO to be an ozone precursor and have exempted it from ozone precursor status.  However, ambient CO concentrations in much of California are typically several parts per million – considerably higher than precursor VOCs, which are collectively present at several hundred parts per billion of carbon.  Consequently, despite its low specific reactivity, CO may still contribute significantly to the formation of ozone.  This is a particularly important issue in the Bay Area, which was recently re-designated by EPA as nonattainment for ozone.  Further, the NSR Manual requires that ozone precursors be evaluated in the environmental analysis required under the top-down BACT analysis.

Two studies have modeled the contribution of VOCs and CO to ozone formation at various VOC/ NOx ratios.  The results are summarized in Table 5.

In the Los Angeles study, the initial composition of the atmosphere was selected to represent summertime conditions in Los Angeles -- 1,100 ppb of nonmethane hydrocarbons (“NMHC”) and 1,500 ppm of CO expressed as carbon.  The results indicate that CO contributes 5% to ozone formed under conditions representative of the Los Angeles Basin.

In a similar study in Atlanta, initial conditions were selected to represent typical center city values -- 816 ppb of VOCs and 1,200 ppb of CO expressed as carbon.  CO contributed 17.5% to the 209 ppb ozone peak.  The considerably larger contribution of CO to ozone in Atlanta compared to Los Angeles is likely due to several reasons: First, the initial CO/NMHC ratio was higher in Atlanta (1.47 vs. 1.36).  Therefore, CO accounted for a somewhat larger fraction of total carbon in Atlanta than in Los Angeles.  Second, the Atlanta model included a gradual increase in mixing height during the day, as well as the presence of 500 ppb of CO aloft, compared to 30 ppb of VOC aloft.  Thus, mixing caused greater dilution of VOC than CO.  Third, the VOC composition in Atlanta contained lower fractions of highly reactive species, particularly of alkenes.  This would tend to reduce overall ozone production, and also increase the relative importance of less reactive species, such as CO, methane, and alkenes.

Thus, while CO is a relatively weak ozone precursor compared to many organic compounds such as alkenes, the concentration of CO is substantially higher than other precursor compounds.  Therefore, as demonstrated by the two studies summarized in Table 5, CO can contribute substantially to atmospheric ozone.

The relative ozone formation potential of CO from Contra Costa Power Plant can be estimated and compared to that of VOC emissions using the relative reactivity scale developed and routinely updated by Carter.  The “incremental reactivity” of a VOC (grams of ozone per gram of VOC) has become an established method of quantifying and comparing ozone formation potential under specific atmospheric conditions.  Thus, the VOC equivalents of CO emissions can be conservatively estimated from the incremental reactivity of CO relative to propane, the least reactive compound considered a VOC by EPA.

Most recent reactivity data indicate that the mass-based reactivity of propane exceeds that of CO by a factor of 9 to 10.  The ratio of reactivity of two different ozone precursors varies with atmospheric conditions, particularly the VOC/ NOx ratio.  However, the relative reactivity of poorly reactive compounds, such as CO and lighter alkanes, such as propane, are not very sensitive to atmospheric composition.  Thus, using a VOC-equivalency factor of 0.1 for CO represents the most conservative choice for assessing the relative ozone formation potential of CO emissions because it is based on propane.  Consequently, the ozone-forming potential of permitted CO emissions from Contra Costa Power Plant of 259.1 ton/yr (PDOC, p. 8) corresponds to about 29 ton/yr of VOC emissions.

The actual contribution of CO to ozone formation, compared to more reactive VOCs, could be larger because the reactivity scales do not consider the fact that poorly reactive compounds such as CO have a longer effective residence time in the atmosphere, compared to more reactive species which are more rapidly converted, which may increase their total yield compared to more reactive compounds.  Thus, during inversions and other conditions when atmospheric dispersion is poor, CO and alkanes will contribute, on a per mass basis, more to ozone formation than projected from their incremental reactivity.  An assessment of the impact of such conditions on the relative ozone formation potential of CO can only be evaluated by modeling on a case-by-case basis.  However, the above discussion suggests that CO emissions from Contra Costa Power Plant would contribute emissions of VOC equivalents of at least 29 ton/yr.

The formation of ozone precursors must be considered in the environmental analysis required as part of the top-down process.  In fact, the NSR Manual specifically contemplates that precursor compounds be considered in the BACT analysis, as is demonstrated by the following statement:

“For example, the use of certain volatile organic compound (VOC) control technologies can increase nitrogen oxides (NOx) emissions.  In this instance, the reviewing authority may want to give consideration to any relevant local air quality concern relative to the secondary pollutant (in this case NOx  in favor of one having less of an impact on ambient NOx concentrations.”  (NSR Manual, p. B.49.)

In sum, CCPP’s CO emissions would result in the formation of about 29 ton/yr of ozone in an area that currently violates the federal and California ozone standard.  Thus, a CO BACT limit more stringent than 6 ppm is warranted.

# VOC Limit is not BACT

The District established BACT for POCs as 2 ppmvd @ 15% O2 averaged over 1 hour based on CARB's Guidance Document.  In making this determination, the District erroneously eliminated from consideration or overlooked source tests that suggest that BACT for POCs is lower.  (MEC PDOC, p. 11.)  Substantial evidence, not considered by the District, demonstrates that 2 ppmv is not BACT for this Project’s POC emissions.  The evidence reviewed below collectively indicates that BACT for POCs is a limit of no more than 0.1 ppmv based on the Crockett and River Road source tests.

In spite of its CO compliance problems, the Crockett facility achieved 0.007 ppm in one test and 0.041 in the other (CARB 9/99, Table C-12).  These source tests show that emission levels are much lower than the BACT level of 2 ppm selected by the District as BACT for POC.  The low POC emission levels achieved at Crockett were confirmed at the River Road Generating Project, a 248-MW GE Frame 7FA turbine that source tested at 0.0 ppm [sic] at 15% O2.  (Ex. 25.)  These two units are comparable to Contra Costa Power Plant with respect to size, operation mode, and fuel composition.  Thus, the District should have selected a much lower POC limit than 2 ppm as BACT for the CCPP.

The CARB Guidance Document also reports much lower achieved in practice POC limits including <0.8 ppmv at Bear Mountain and <0.67 to <0.71 ppmv at Brooklyn Navy Yard.  Although the turbines are smaller than proposed by CCPP, the size and load of the turbine do not affect the ability of an oxidation catalyst to control either CO or POCs.  This is demonstrated by four sets of source tests which were conducted at both 50% and 100% loads.  These tests show comparable POC levels and performance of the oxidation catalyst at both loads.  The POC (and CO) limit that can be achieved by an oxidation catalyst depends on the stack gas composition and the design of the oxidation system, not on the size of the turbine or its operating mode.  The operating mode is normally accommodated in the design of the oxidation catalyst by simply increasing the volume of catalyst to control potential excursions during low load operation.

Similarly, the District ignored the lower POC BACT limits that have been established for Calpine’s Sutter Power Project (1.0 ppmv) and for La Paloma Generating Company (1.1 ppmv).   As discussed above, to qualify for inclusion in the top down process, an emission limit need only be specified in a permit, not demonstrated in practice. Therefore, the District should have explicitly considered these lower permit limits in its BACT decision.

# startup and shutdown emissions are improperly permitted

The District did not consider startup and shutdown emissions in its BACT analysis.  Further, the proposed limits are inconsistent with vendor data.  These two issues are discussed below.

## BACT Has Not Been Required For Startup And Shutdown Emissions

During startups and shutdowns, combustion temperatures and pressures change rapidly, resulting in inefficient combustion and higher emissions of NOx, CO, and VOCs than during steady state operation.  Further, during much of this transient period, the flue gas temperatures are lower than the design temperature of the SCR and oxidation catalysts, reducing their removal efficiency and further increasing emissions.

The U.S. EPA has consistently defined startup and shutdown to be part of the normal operation of a source.  (Bennett 9/28/82, 2/15/83.)  The U.S. EPA has also consistently concluded that these emissions “should be accounted for in the design and implementation or the operating procedure for the process and control equipment.  Accordingly, it is reasonable to expect that careful planning will eliminate violations on emission limitations during such periods.”  (Ibid.)  Furthermore, the new source performance regulations under the Clean Air Act provide as follows:

At all times, including periods of startup, shutdown, and malfunction, owners and operators shall, to the extent practicable, maintain and operate any affected facility including associated air pollution control equipment in a manner consistent with good air pollution control practice for minimizing emissions.  (40 CFR § 60.11(d).)

CARB has also stated that “the BACT decision should consider control of emissions during such periods of operation.”  (CARB 9/99, p. 34.)  Hence, the Project’s startup and shutdown emissions should be considered in the BACT analysis, and all reasonable measures should be taken to minimize these emissions.  (Rasnic 1/28/93.)

The draft permit in the PDOC includes separate limits for NOx and CO for hours in which startups and shutdowns occur.  The EPA does not generally concur with this method of limiting startup and shutdown emissions.  (Rasnic 1/28/93, p. 2.)  The record contains no evidence that the Project’s startup and shutdown emissions were evaluated in the BACT analysis, or that efforts would be made to assure that these emissions are appropriately controlled.

The proposed permit limits for the Project’s startup and shutdown emissions are much higher than levels that are routinely achieved using SCONOx.  SCONOx is capable of achieving much lower emissions during startup and shutdown because it is fully operational at much lower temperatures, typically 300oF, than other catalytic-based systems.

The Applicant's turbine vendor could optimize the startup/shutdown process to reduce the Project’s startup and shutdown emissions.  In addition, there are a number of controls available to the Applicant that could be used to satisfy BACT and reduce startup and shutdown emissions.  These include the following:

- Use of an auxiliary boiler or other source of sealing steam to reduce startup time.

- Use of a stack damper to keep the HRSG hot during shutdown;

- Early injection of NH3 into the SCR;

- Use of alternatives to low-NOx combustor technology, such as XONON, which can achieve 3 ppm NOx at 15% O2 as currently proposed by Pastoria;

- Use of more efficient primary control technologies, such as SCONOx; and/or

- Use of other methods to more quickly heat up the catalysts in the control technologies.  (CARB 9/99, p. 35)

## Startup And Shutdown Emissions Are Inconsistent With Vendor Data

The District established startup and shutdown emissions in draft Permit Condition 21, apparently calculated by multiplying the hourly startup emission rate by the estimated startup time.  (MEC AFC, Supplement C, Table 8.1A-2.)     However, the Applicant's data that the District relied on is inconsistent with vendor data submitted in other cases.  The following table compares the proposed permit limits with data supplied by Westinghouse for its 501F machine in other cases:

EMISSIONS  (lbs per event per turbine)

NOx                              CO                            POC

Cold	Hot		Cold	Hot		Cold	Hot

TMP		556	153		1163	853		146	115

Sutter		306	170		1466	902		-	-

MSEP		350	120		1825	970		200	120

CCPP		240	80		2514	902		48	16

These data indicate that the proposed permit limits for NOx and POCs are substantially lower than vendor-supplied data while the CO cold start limit is substantially higher.  Therefore, the District should request supporting vendor data and verify that the proposed permit limits are reasonable.  The District should also require that the continuous emissions monitoring cover startup and shutdown periods, and require the Applicant to use a CEM system, which is capable of producing accurate measurements during the varying conditions, which will exist during startups and shutdowns.

.

# PM10 EMISSIONS ARE IMPROPERLY ESTIMATED AND PERMITTED

## The Level of PM10 Emissions is Understated in the PDOC

1. PM10 emissions from the gas turbine and duct burners

The PDOC is based on a PM10 emission rate of 26 lb/hr (PDOC, p. 30, Condition 24(d)). This emission rate is used to determine the need for PM10 offsets and PSD review, both of which are triggered if emissions exceed 100 ton/yr.  The total PM10 emissions, based on this limit, are 112.2 ton/yr.

A number of power plant applicants have recently proposed similarly low PM10 limits based only on the filterable fraction to reduce PM10 offset liability (e.g., Sunrise, Moss Landing), assuming that the condensable fraction of PM10 is negligible.  They are gambling that exceedances will not be detected because only annual or less frequent source testing is required, during which operations are typically optimized to minimize emissions immediately prior to a source test. We reviewed source tests of similar facilities to determine whether the proposed limit could reasonably be expected to be met (see Table 6).

It is unlikely that the exceedances will be detected, unless a continuous emission monitor is used.  It is well known that “[m]anual stack tests are generally performed under optimum operating conditions, and as such, do not reflect the full-time emission conditions from a source.”  (40 FR 46241 10/6/75.)  A widely used handbook on CEMs notes, with respect to PM10 source tests, that: Due to the planning and preparations necessary for these manual methods, the source is usually notified prior to the actual testing.  This lead time allows the source to optimize both operations and control equipment performance in order to pass the tests.”  Therefore, it is unlikely that violations of the proposed 26-lb/hr limits would be detected.

The NSR Manual requires that “BACT emission limits or conditions must be met on a continual basis at all levels of operation...and be enforceable as a practical matter.”  (NSR Manual, p. B.56.)  PM10 is routinely continuously monitored in Europe.  The EPA has required continuous PM10 monitoring on incinerators and has proposed Performance Specification 11 for their certification.  Therefore, we recommend that the District either require continuous monitoring for PM10.

## The PDOC understates the PM10 increment consumption by CCPP

### Corrected emissions factors

The PDOC may also have underestimated the PM10 emissions associated with the cooling tower, since it relies on an unverified drift fraction. And of course the PDOC makes no allowance at all for PM10 due to ammonium nitrate formed from

Ammonia slip due to use of SCR for NOx control. After making the appropriate corrections, the District should recompute the incremental increase in maximum PM10 concentrations due to CCPP.

### Alternative modeling approaches

The PM emissions from the cooling towers contribute significantly to the ambient air concentrations of PM10 concentrations. The effluents have low exit temperatures, low exit velocities and correspondingly are low in momentum and buoyancy. When ISC3 is used to model the impact of these emissions as point sources, as was done in the Applicant’s submission, ISC3 models these as point sources and the Briggs plume rise equations are used.  The plumes are predicted to have significant plume rise and the ground level concentrations are predicted accordingly.  Observing that the releases often show little buoyancy, an alternative method of modeling the emissions is to assume they emanate from a series of volume sources based upon the dimensions of the individual cooling towers. This method better simulates the observation that there is little plume rise.  When volume source configurations replace the point source approximations in ISC3, the predicted concentrations increase substantially, from a maximum value of about 8 g/m3 on a 24-hour basis to a value of 61 g/m3. A value of 61 g/m3 would constitute an exceedance of the Federal PSD increment of 30 g/m3 for PM10.  Because of the sensitivity of the predicted concentrations to the way that the cooling tower emissions are modeled, the District should attempt to use alternative approaches to test whether the cooling towers would cause an exceedance of a PSD increment.

# VII.        THE health risks OF CCPP ARE SIGNIFICANT

The Applicant evaluated the public health impacts of the Project to comply with the District's "Toxic Risk Management Policy"  ("TRMP") and to satisfy its AB2588 LORS obligation under the Warren Alquist Act.  The District's policy requires the installation of Toxics Best Available Control Technology ("TBACT") if the cancer risk is greater than one in one million or if the chronic hazard index is greater than one.

The most recent version of the Applicant's analyses underestimate health risks.  When the errors and omissions discussed below are corrected, the Project is found to result in significant cancer, chronic, and acute health impacts, requiring additional mitigation and/or denial of the Project.

## Cancer Impacts From The Turbine Are Significant

The MEC Applicant estimated incremental cancer risk (number of additional cancers per million people exposed) using the CAPCOA Risk Assessment Guidelines.  (MEC AFC, § 8.6.)  Incremental cancer risk is calculated by estimating toxic emissions, modeling these emissions to estimate corresponding ambient concentrations, multiplying the modeled ambient concentration by a cancer unit risk factor, and summing over all compounds.  A cancer unit risk factor expresses an individual’s risk of contracting cancer for a given amount of pollutant breathed.  It is expressed as the cancer risk per amount of a pollutant in a volume of air (i.e., risk per g/m3).  Risk factors are published on the Office of Environmental Health Hazard Assessment's ("OEHHA's") website.

### Partial Load Operation

The Applicant's calculations, summarized in the PSA, suggest that the total cancer risk is 0.86 in one million, which is less than the significance threshold of one in one million.  These calculations assume that both turbines are operating simultaneously at full load with the duct burners firing.  However, emissions of some toxic compounds are substantially higher during reduced loads, such as occur during startup, shutdown, and partial load operation, than during routine operation.  The following references the MEC project – CARE contends the applicant and CEC have a duty to provide similar analysis in the case of the CCPP.

The Gas Research Institute ("GRI") investigated the effect of load on criteria and toxic pollutant emissions from nine gas turbines including a large Frame 7 turbine.  This study found that emissions of benzene, toluene, formaldehyde, methane, and total nonmethane hydrocarbons increase with load.  Emissions of formaldehyde, a carcinogen, increased dramatically, by up to a factor of 343 when the load was reduced from 100% to 20%.  For the 750 MW GE Frame 7, the formaldehyde emission factor increased from 15 lb/1012 Btu to 7,539 lb/1012 Btu, or by a factor of 503, and the formaldehyde emissions increased from 0.11 to 16.08 tons/yr or by factor of 146, when the load was reduced from 100% to 30%.  (GRI 8/96, Table S-5.)  This substantial increase in formaldehyde emissions during reduced load operation was not taken into account in the Applicant's risk calculations.

The maximum annual emission calculations in the PDOC & PSA are based on 83 1.5-hour hot startups per year, 28 3-hour cold startups per year, and 111 shutdowns per year.  (PDOC, p. 7)  Therefore, the facility will be operating at reduced load during startups for up to 233 hours per year, or perhaps even more.  One or both turbines may also operate at reduced load for additional hours during non-startup periods, which are ignored here, but which would generally increase formaldehyde emissions beyond those claimed below.  Using the MEC Applicant's formaldehyde emission factor of 0.11 lb/MMscf (MEC PDOC, Table B-8) for 7,928 hour per year (8,760 hr - 832 hr = 7,928 hrs) and an emission factor that is 146 times higher for the 832 hours of partial load operation results in annual load-weighted formaldehyde emissions that are 14.8 times higher than those evaluated by the Applicant in the cancer risk analysis.  This increases the cancer risk due to formaldehyde alone from 6.30x10-8 to 9.3x10-7.

The change in formaldehyde risk alone would increase the total cancer risk of the Project from 0.2 in one million (0.20x10-6) assumed in the MEC PDOC (Table 7) to slightly over one in one million (1.07 x10-6). Acetaldehyde is an aldehyde that is chemically similar to formaldehyde.  Assuming that it increases in like fashion, the cancer risk from acetaldehyde alone would increase from 1.76 x 10-8 to 1.99 x 10-7.  Benzene and possibly other toxics would also increase, further increasing cancer risk.  This exceeds the significance threshold of one in one million and requires that TBACT be installed.  At a minimum, TBACT would be either an oxidation catalyst or SCONOx, both of which have been demonstrated to reduce aldehydes.

We note here that the MEC PDOC condition purporting to eliminate formaldehyde emissions to 1898 pounds per year (proposed condition 26) is no substitute for TBACT. Compliance with proposed condition 26 is to be done by calculating formaldehyde emissions based on “the highest emission factor determined by any source test” of the turbines and HRSGs (proposed MEC PDOC condition 29). Unless the source testing is done during startup or low-load conditions it will not reveal the high formaldehyde emission rates identified by GRI. A refinement to condition 29 requiring source testing at low load and/or start-up conditions should be an additional MEC condition, in addition to requiring TBACT for aldehydes.

### Dry Low NOx Combustors

The Applicants used CARB's CATEF database to estimate toxic emissions of all chemicals except acrolein. We suspect that the combustors on the turbines used to develop these emission factors were based on the diffusion-flame principle and were not equipped with pre-mixed, dry low NOx combustors, which are now widely used to control NOx.  The CATEF database is based on measurements that were made between 1988 and 1992, when steam injection was predominately used to control NOx rather than pre-mixed combustors.

The GRI study indicates that pre-mixed low NOx combustors increase emissions of formaldehyde by about a factor of 6.6 during full load and by a factor of 11.4 during reduced load, compared to the same turbine without a low-NOx combustor. (Ex. 44 Table S-5, p. 8.)  Benzene emissions are almost 40 times greater during reduced load operation for a turbine with low-NOx combustors as for the same kind of turbine without them, and are over twice as great during full-load operation when a low NOx combustor is used.

The Project proposes to use a dry low NOx combustor to control NOx.  Therefore adjustment factors have been included in Table 8 to account for increased emission associated with turbines using low-NOx combustors.

### Other Carcinogens

### The Applicant's analysis only considers five carcinogens: acetaldehyde, benzene, 1,3-butadiene, formaldehyde, and PAHs.  However, dioxins, furans, hexavalent chromium, lead, and nickel are

present in the emissions from Frame 7 machines.  (ESI 6/30/92.)  We did not include them in our analysis because cancer risks exceed significance thresholds without them.  However, the Applicant should be required to revise its risk calculations to include these additional substances, because they may make a significant contribution when considering controls to reduce risks from the volatile organic compounds discussed above.

## Noncancer Health Impacts From Turbines Are Significant

The Applicant estimated Noncancer health impacts using the hazard index approach.  A hazard index is the ratio of the ambient concentration, estimated by modeling, to the reference exposure level or REL, which is the concentration deemed by OEHHA as being safe.   The total hazard index is the sum of the indices for individual compounds.  If the chronic hazard index exceeds one, impacts are significant and TBACT is required.  The District does not evaluate the acute hazard index, but the Energy Commission typically considers an acute hazard index greater than one as significant.  The Applicant estimated a chronic hazard index of 0.04.  (PSA, p. 84 Table 3.)  As discussed above, this index is underestimated because the Applicant's calculations do not take into account-increased emissions during partial load operation and the use of a DLN combustor.  In addition, the Applicant made a questionable adjustment to the acrolein emission factor.

### Acrolein Emission Factor

The Applicant originally estimated acrolein emissions using the CARB emission factor of 2.37x10-2 pounds per million standard cubic feet of gas combusted ("lb/MMscf").  However, these original calculations were based on outdated acute reference exposure levels ("acute RELs").  Thus, the Energy Commission directed the Applicant to revise their health risk assessment to use current acute RELs.  (MEC CEC Data Request 63, 8/23/99, p. 62.)  This increased the acute hazard index from 0.16 (MEC AFC, Table 8.6-6) to 1.05, exceeding the significance level of one.  Therefore, the Applicant apparently reduced the acrolein emission factor from 2.37x10-2 to  6.43x10-3 to reduce acute health impacts below the significance level of one.  (MEC AFC, Supplement C, Table 8.1A-3.)  This adjustment is wholly unsupported.

Both the Energy Commission Staff (MEC CEC Data Request PH-1, April 7, 2000) and the District (Jang 3/2/00) requested a clarification of this change.  The MEC Applicant explained that the original emission factor was based on four source tests, only one of which was conducted on a Frame 7 machine.  Therefore, the MEC Applicant used the single source test on the Frame 7, which lowered the acrolein emission factor from 2.37x10-2 to 6.43x10-3 lb/MMscf.  This is not justified as explained below.

Acrolein is the most toxic compound emitted by the gas turbines.  It is a double-bonded aldehyde which causes eye, nose and throat irritation.  It has the lowest acute and chronic reference exposure level among all of the substances emitted by the turbine.  Therefore, very small concentrations of acrolein, much smaller than any other compound emitted by the Project, will result in significant health impacts.

The MEC Applicant's risk assessment relied on a revision to the acrolein emission factors reported in CARB's CATEF database.  However, the acrolein emission factor in this database was based on source tests in which acrolein was measured by CARB Method 430.  (CARB 4/96.)  CARB has recently published an advisory that states: "any data or results, based on the use of M430 to determine acrolein...are suspect and should be flagged as nonquantitative wherever they appear."  (CARB 4/28/00.)  This method has been validated for only formaldehyde and acetaldehyde and substantially underestimates acrolein concentrations.

CARB Method 430 measures acrolein by reacting it with 2,4-dinitrophenylhydrazine ("DNPH") acidified with hydrochloric acid, which converts the acrolein into its hydrazone derivative.  The hydrazone derivative is then analyzed by high performance liquid chromatography.  However, the hydrazone derivatives of double-bonded aldehydes such as acrolein are not stable under acidic conditions and rapidly degrade.  The acrolein hydrazone derivative begins to degrade almost immediately.  After 30 minutes,  60% is degraded, after 1 hour, 70% is degraded, and after 48 hours, 93% is degraded. (Freeman 1993.)  Typically, it takes four hours to collect a sample.  One to two weeks typically elapse between sample collection and analysis.  Therefore, well over 90% of the acrolein is lost before the sample is analyzed.

The MEC Applicant justified using the Frame 7 emission factor "[b]ecause of the differences in combustion and control technology between the frame turbines and other turbines tested, there is no reason to believe that the test results from the other turbines are more representative than the test results from the frame turbine."  (MEC response to Staff Data Request PH-1, 4/7/00, pp. 1-2.)  However, differences in the elapsed time between sample collection and extraction among the four source tests creates far more variability among acrolein emissions than turbine type.   Thus, it is impossible, given this situation, to conclude that any one of the four measurements is any more representative of Frame 7 machines than any other.  In fact, it is a fair bet than none are representative and all are underestimates.  Therefore, none of the data should have been discarded.   To address these analytical problems, we multiplied the acrolein emission factor by ten to adjust for the degradation that occurs between sample collection and extraction.  We believe that this is conservative and underestimates actual acrolein emissions.

Using the average CATEF emission factor (2.37x10-2 lb/MMscf) as required by CARB and increasing it by a factor of ten increases the acute hazard index from 0.33 reported in the MEC PDOC to 1.7, which is significant.  Likewise, these same two changes (CATEF data instead of the MEC Applicant’s unilateral adjustment of it; factor of ten increase to reflect CARB 430 under measurement of acrolein) increase the chronic hazard index from 0.06 reported in the MEC PDOC to 0.93.  Similar analysis needs to be provided in the CCPP FDOC & FSA.

In addition to using the wrong emission factor and failing to adjust it to account for acrolein degradation, the MEC Applicant also failed to consider startup and shutdown conditions and the use of DLN combustors, as discussed above.  Each of these factors further increases the chronic and acute hazard indices.  Incorporating all of these factors, as explained in Table 8, increases the acrolein hazard index values in Table 7, which are far above the permissible level of 2. Even if acrolein emissions are overestimated by factors of ten to one hundred, these hazard indices would still exceed the significance threshold of one by a large margin, requiring the use of TBACT. Put another way, if any of several acrolein emissions adjustment factors listed in Table 8 are appropriate, then acrolein emission adjustment factors listed in Table 8 are appropriate, then acrolein will have an acute hazard index greater than one.

- The Acute Hazard Index for Fermaldehyde Also Exceeds One

Acrolein is not the only compound shown in Table 7 with a revised acute hazard index greater than one. The index for formaldehyde also exceeds one, providing yet another reason (besides its cancer risk) to require BACT for formaldehyde.

# OTHER ISSUES

## Contemporaneous Emission Reduction Credits (CERCs) vs. Offsite Emission Reduction Credits and the Nexus with Civil Rights

CARE contends that the CCPP threatens to inflict further disparate impacts on low-income and minority communities in the adjacent community of Pittsburg, and portions of the western area of the City of Antioch as shown in Figure 1. These disparate impacts

Figure 1 Minority Distributions as a Percentage of Total Population

These disparate impacts are the subject of CARE’s complaint against the CEC, BAAQMD, and CARB, before the EPA Office of Civil Rights. One remedy examined in CARE’s amendment 2 includes the use of SCONOx emission control technology on the proposed Delta Energy Center (98-AFC-3) and the Los Medanos Energy Center (98-AFC-1). CARE’s complaint calls for remedies including local mitigation specifically targeted towards the environmental justice area as defined by the Pittsburg Unified School Resolution 99-32. There are portions of Antioch where low-income children are exposed to these disparate impacts as identified in Figure 2. CARE provides evidence of disparate impacts on Contra Costa County in comparison with surrounding counties with lower concentrations of low-income and minority populations in figure 3. CARE presents

the results from CARB comparing seven criteria air pollutants from adjacent counties in 1996 to demonstrate the disparate impacts to Contra Costa County.

“Emissions of seven criteria air pollutants are compiled in this report. The pollutants are total organic gases (TOG), reactive organic gases (ROG), carbon monoxide (CO), oxides of nitrogen (NOx), oxides of sulfur (SOx), particulate matter (PM), and particulate matter with an aerodynamic diameter of 10 micrometers or smaller (PM10). Some of these pollutants are precursors to other pollutants. For example, oxides of nitrogen and reactive organic gases are precursors to the formation in the atmosphere of oxidants such as ozone. Some of the oxides of nitrogen and oxides of sulfur emitted in the gaseous state are converted to nitrate and sulfate particulates, respectively.”

Figure 3 Total emissions of criteria pollutants from stationary sources by county.

Various BAAQMD regulation spell out the benefits of using contemporaneous emission reduction credits onsite to mitigate emissions. In the case of the CCPP these benefits provide CCPP an opportunity to eliminate the need for purchasing offsite ERCs by providing local environmental benefits that outweigh any adverse impacts on low-income and minority populations affected by the CCPP.

BAAQMD Regulation 2-2-214 defines Emission Offsets as,

“Emission reduction credits which are used to mitigate cumulative increases of emissions. Emission offsets are emission reduction credits, from the District Emissions Bank, approved in accordance with Regulation 2, Rule 4; emission reduction credits from adjacent Districts, provided the applicant demonstrates that the requirements of Clean Air Act Section 173(c)(1) (42 U.S.C. Section 7503(c)(1)) and Health and Safety Code Section 40709.6 have been met or do not apply, or onsite contemporaneous emission reduction credits occurring after the submittal of an application for a new or modified source but prior to the issuance of the permit to operate any such source, calculated in accordance with Section 2-2-605. Notwithstanding any existing permit conditions, that portion of an NSR emission cap, which was based on an APCO approved alternative baseline, may not be used as a source of offsets unless the proposed reduction is calculated in accordance with procedures specified in Section 2-2-605. (Amended 6/15/94; 5/17/00)”

BAAQMD Regulation 2-2-245 defines “Fully Offset” as,

“An emission cap or emission rate contained in a permit condition is fully offset if offsets were provided for the entire amount of the emission cap or emission rate, and the entire amount of offsets is composed of contemporaneous emission reductions or banked emission reduction credits. (Adopted May 17, 2000)

BAAQMD Regulation 2-2-302 provides an example of “Offset Requirements” for Precursor Organic Compounds and Nitrogen Oxides, NSR as,

“Except as provided by Sections 2-2-313 or 421, before the APCO may issue an authority to construct or a permit to operate for a new or modified source at a facility which emits 50 tons per year or more or will be permitted to emit 50 tons per year or more, on a pollutant specific basis, of precursor organic compounds or nitrogen oxides, federally enforceable emission offsets shall be provided, for the emission from the new or modified source and any pre-existing cumulative increase, minus any onsite contemporaneous emission reduction credits determined in accordance with Section 2-2-605, at a 1.15 to 1.0 ratio; additionally, the applicant must reimburse the District Small Facility Banking Account for any unreimbursed offsets previously provided by the District, at a 1.0 to 1.0 ratio.

Both the PDOC and PSA fail to properly examine the use of contemporaneous emission reduction credits onsite to mitigate emissions, and the associated benefits to the local environment and affected low-income and minority populations.

- Nexus of Biological Impacts, Habitat Conservation Plan, USFWS Section 7 Biological Opinion, and the EPA PSD Permit.

In it’s consideration of the PSD permit for this project the CEC and air district failed to specify the effects of the proposed HCP being developed as part of this project which is the subject of section 7 consultations, and a resulting biological opinion, from the US Fish and Wildlife Service (USFWS). CARE requests a more thorough explanation of the effect of consultation with USFWS on the scheduled issuance of the PSD permit for this case. In the MEC case the Commission and District decided to bifurcate the FDOC and PSD permit. The MEC FDOC was issued prior to completion of the PSD permit, because the EPA denied a PSD permit in the Three Mountain Power Plant Project (99-AFC-2) until EPA had an opportunity to review and concur with the USFWS biological opinion in this case.

CARE has provided a copy of the PDOC and PSA for the CCPP to Dr. K. Shawn Smallwood a biologist who consulted with CARE on the MEC project. Dr. Smallwood has provided written comments and a copy of his bio & vitae. CARE hereby incorporates these comments by reference in this case.

Michael E. Boyd 12-01-00              Jim MacDonald 12-01-00

President-CARE		         Contra Costa Director- CARE

CURE is the acronym for the California Unions for Reliable Energy.  CURE has taken no position on the CCPP project. However, the comments below on the CCPP project draw on various public documents filed by CURE in the Elk Hills, Sunrise, and Three Mountain siting cases. These documents include:

a. Letter from Lizanne Reynolds, Adams Broadwell Joseph & Cardozo, Re: Comments on Draft PDOC for the Elk Hills Power Project (ATC #990210), January 17, 2000.

b. Elk Hills, CEC Docket No. 99-AFC-1, Exhibit 44, Testimony of J. Phyllis Fox, Ph.D. on Behalf of the California Unions for Reliable Energy on Air Quality Impacts of the Elk Hills Power Project, May 8, 2000.

c. Letter from Katherine S. Poole, Adams Broadwell Joseph & Cardozo, Re: Comments on Preliminary Determination of Compliance for the Sunrise Cogeneration and Power Project, August 28, 1999.

d. Letter from Katherine S. Poole, Adams Broadwell Joseph & Cardozo, Re: Comments on PSD Permits SJ 99-01, SJ 78-16 and SJ 78-17 (Sunrise), January 7, 2000.

e. Letter from Lizanne Reynolds, Adams Broadwell Joseph & Cardozo, Re: Comments on the Draft PSD ATC/PDOC for the Three Mountain Power Project (ATC #99-PQ-01), February 3, 2000.

f. Letter from Mark R. Wolfe, Adams Broadwell Joseph & Cardozo, Re: PSD/ATC/FDOC for the Three Mountain Power Plant Project -- Supplemental BACT Analysis for SCONOx, May 28, 2000.

U.S. EPA, New Source Review Workshop Manual.  Prevention of Significant Deterioration and Nonattainment Area Permitting, Draft, October 1990.

CARE is not alone in making this point. The CEC staff in their CCPP PDOC comments has also called on the BAAQMD to perform a top-down BACT analysis. CEC, 5/16/2000, Therkelsen to Garvey letter re CCPP PDOC.

Letter from Matt Haber, Chief, Permits Office, to statewide air pollution control districts and others, March 24, 2000.

Letter from Matt Haber, Chief, Permits Office, U.S. EPA, to Robert Danziger, President, Goal Line Environmental Technologies (March 23, 1998).

SCAQMD, Staff Report for Best Available Control Technology Guidelines Update (Phase IID), June 12, 1998.

U.S. EPA, New Source Review Workshop Manual.  Prevention of Significant Deterioration and Nonattainment Area Permitting, Draft, October 1990.

Removal efficiency depends on temperature and space velocity.  The space velocity was reduced from about 18,000 hr-1 to 10,000 hr-1 by adding more catalyst.  The same performance could be achieved at Elk Hills with a space velocity of 22,000 hr-1 because the catalyst would be located in the HRSG at a temperature of about 600 F, compared to 300 F at the Federal Facility, which was a retrofit application.

See CURE comments submitted to the U.S. EPA on the Sunrise Project, to the Shasta County Air Quality Management District on the Three Mountain Power Project, and to the San Joaquin Valley Unified Air Pollution Control District on the Elk Hills Project. These comments are items a and c-f in footnote 1, supra.

A lower NOx limit could be readily achieved at the Federal Facility by increasing the frequency of catalyst washing.  The peaks and valleys shown during sustained operation during the latter half of 1999 correspond to catalyst washing events.  Sulfur combustion byproducts in the flue gas can deactivate the SCONOx catalyst.  This can be addressed in two ways.  First, the catalyst can be periodically washed with water.  This procedure is used at the Federal Facility.  Second, a sulfur removal catalyst, SCOSOx, can be installed upstream of SCONOx.  SCOSOx is used at the Genetics Facility.   The choice between catalyst washing and SCOSOx is a purely economic decision.  Both are commercially available, and both can be designed to achieve a lower NOx limit than currently achieved at the Federal Facility.

Memorandum from John Seitz, Director, Stationary Source Compliance Division, Office of Air Quality, Planning and Standards, U.S. EPA, to David Kee, Director, Air and Radiation Division, U.S. EPA Region V, Subject:  Cut-off Date for Determining LAER in Major New Source Permitting (February 24, 1989).

Letter from Anupom Gangule, Senior Manager, Stationary Source Compliance, South Coast AQMD, to Steve Weinman, Director, Standardization, ASME International, Subject:  Lowest Achievable Emission Rate (LAER) for Gas Turbines, May 26, 1998.

Delta Air Quality Services, Inc., NOx Stratification Test Report.  Sunlaw Cogeneration partners I Federal Cold Storage Cogeneration Facility, June 29, 1998.

?  The South Coast AQMD concludes that 2 ppmvd averaged over 3 hrs is equivalent to 2.5 ppmvd averaged over 1 hr.  (South Coast AQMD 5/12/98, p. 3-4).

Letter from Matt Haber, Chief, Permits Office, U.S. EPA, to Robert Danziger, President, Goal Line Environmental Technologies, March 23, 1998.

Marsh USA Inc., ABB SCONOx System Insurance Review, Prepared for ABB Environmental Systems, October 6, 1999.

SCONOx was ultimately not installed on this Project because at the time construction commenced, in November 1999, because ABB had not completed their testing and scaleup program.  This program has since been completed and, thus, there should be no commercial impediment to the future use of SCONOx.

San Joaquin Valley Unified Air Pollution Control District, Notice of Determination of Compliance for La Paloma Generating Company, LLC Project Number: 980654, May 26, 1999.

Letter from John P. DeVillars, Regional Administrator, Region 1, U.S. EPA, to Robert Varney, Commissioner, Department of Environmental Services, New Hampshire, Subject:  Recent SCONOx Pollution Prevention Control System Development, December 20, 1999.

U.S. EPA, OAQPS Control Cost Manual, 5th Ed., Report EPA 453/B-96-001, February 1996.

ONSITE SYCOM Energy Corporation, Cost Analysis of NOx Control Alternatives for Stationary Gas Turbines, Report Prepared for U.S. Department of Energy, October 15, 1999.

Elk Hills, Docket No. 99-AFC-1, Exhibit 44, May 8, 2000, Table 1.

Letter from Matt Haber, Chief, Permits Office, EPA Region 9, to Dennis J. Champion, Project Permitting Manager, Elk Hills Power, Re: Prevention of Significant Deterioration (PSD) Application for Elk Hills Power, LLC, 500 MW Power Plant, February 10, 2000.

San Joaquin Valley Unified Air Pollution Control District (“SJVUAPCD”), Best Available Control Technology (BACT) Policy, November 9, 1999, p. BACT 1-2.

Bay Area Air Quality Management District (“BAAQMD”), BACT/TBACT Workbook.  Guidelines for Best Available Control Technology, June 30, 1995, p. 9.

South Coast Air Quality Management District (“South Coast AQMD”), Draft Best Available Control Technology Guidelines, September 11, 1995, p. 33, Table 4.

South Coast AQMD, Best Available Control Technology Guidelines, Part A: Policy and Procedures, May 21, 1999, p. 10.

Memorandum from Gerald A. Emision, Director, Office of Air Quality Planning and Standards, Subject:  Implementation of North County Resource Recovery PSD Remand, September 29, 1987; Memorandum from Gerald A. Emison, Re: Supplemental Guidance on Implementing the North County PSD Remand, July 28, 1988.

Memorandum from F. Henry Habicht II, Deputy Administrator, Subject:  EPA Definition of “Pollution Prevention,” May 28, 1999.

John H. Seinfeld and Spyros N. Pandis, Atmospheric Chemistry and Physics, John Wiley & Sons, Inc., New York, 1998.

S. Matsuda, T. Kamo, A. Kato, and F. Nakajima, Deposition of Ammonium Bisulfate in the Selective Catalytic Reduction of Nitrogen Oxides with Ammonia, Ind. Eng. Chem. Prod. Res. Dev., v. 21, 1982, pp. 48-52.

J.M. Burke and K.L. Johnson, Ammonium Sulfate and Bisulfate Formation in Air Preheaters, Report EPA-600/7-82-025a, April 1982.

ASME, Low NOx Measurement: Gas Turbine Plants.  Final Report on Review of Current Measuring and Monitoring Practices, Report CRTD Vol. 52, January 11, 1999.

Barbara J. Finlayson-Pitts and James N. Pitts, Jr., Chemistry of the Upper and Lower Atmosphere.  Theory, Experiments, and Applications, Academic Press, San Diego, 1999.

CARB, Guidance for Power Plant Siting and Best Available Control Technology, As Approved by the Air Resources Board on July 22, 1999, September 1999.

California Air Resources Board (CARB), Guidance for Power Plant Siting and Best Available Control Technology, September 1999.

Memorandum from David B. Struhs, Commissioner, Massachusetts Department of Environmental Protection, to Ed Kunch, Re: Best Available Control Technology (BACT)/Lowest Achievable Emission Rate (LAER) for Electric Power Generators, January 29, 1999.

Monterey Bay Unified Air Pollution Control District, Preliminary Determination for Duke Energy Moss Landing LLC, January 7, 2000.

CEC staff, Metcalf PSA, 5/15/2000, p. 41, item 7.

www.baaqmd.gov/permit/bactworkbook/89-2-1.htm.

Letter from Robert L. Therkelsen, Deputy Director, Energy Facilities Siting and Environmental Protection, CEC, to Ellen Garvey, Air Pollution Control Officer, BAAQMD, May 16, 2000.

Letter from Raymond E. Menebroker, Chief Project Assessment Branch, CARB, to Ellen Garvey, Air Pollution Control Officer, BAAQMD, September 1, 1999.

Letter from Stan Mack, Sales Manager, Engelhard, to Bob Giorgis, CARB, July 19, 1999.

Silencing baffles in the gas stream were insulated.  Some of the insulation was pulled out by the gas flow and plugged the CatCO catalyst.  In one case, the maximum allowed backpressure was exceeded, shutting down the unit and damaging the frame.

Letter from Stan Mack, Sales Manager, Engelhard, to Bob Giorgis, CARB, July 19, 1999.

California Air Resources Board, Identification of Volatile Organic Compound Species Profiles, ARB Speciation Manual, 2nd Ed., vol. 1, August 1991 plus updates available from Paul Allen, CARB; U.S. EPA, Air Emissions Species Manual.  Volume I. Volatile Organic Compound Species Profiles, 2nd Ed., PB90-185844, 1990.

Delta, Formaldehyde, Acetaldehyde and Benzene Control Efficiency at Federal Cold Storage March 14, 1997, April 2, 1997.

The vast majority of the organics in turbine exhaust are methane and ethane, which are not ozone precursors and, therefore, not included in ROC.

? Letter from Abe Rosenstein, Englehard Corp., to Chuck Eliason, Tenaska, Re: Tenaska Frederickson Washington Project, December 2, 1992.

John H. Seinfeld and Spyros N. Pandis, Atmospheric Chemistry and Physics, John Wiley & Sons, Inc., New York, 1998, at p. 241; Peter Warneck, Chemistry of the Natural Atmosphere, 2nd Ed., International Geophysics Series, Volume 71, 1999, at p. 256.

W. Carter, Development of Ozone Reactivity Scales for VOC, Journal of the Air and Waste Management Association, v. 44, 1994, pp. 881 et seq.

The atmospheric chemistry of NOx and VOC exhibits significant non-linearity.  Thus, modeling is required for a more quantitative assessment of these factors.

F. Bowman and J. Seinfeld, Ozone Productivity of Atmospheric Organics, Journal of Geophysical Research, v. 99, 1994, pp. 5309 et seq.

Harvey E. Jeffries, Photochemical Air Pollution, In: H.B. Singh (Ed.), Composition, Chemistry, and Climate of the Atmosphere, Van Nostrand Reinhold, New York, 1995, § 9.4.1.

W. Carter, Documentation of the SAPRC-99 Chemical CCPPhanism for VOC Reactivity Assessment, CARB Report, Draft, September 1999.

Federal Register, Revision to Definition of Volatile Organic Compounds - Exclusion of Acetone, v.  60, p. 31633, June 16, 1995.

Personal communication, J. Phyllis Fox, Ph.D. with William Carter, University of California at Riverside, Air Pollution Research Center (909-781-5797), December 1999.

Letter from Kathleen M. Bennett, Office of Air, Noise and Radiation, to Assistant Administrator for Air, Noise and Radiation Regional Administrators, Regions I-X, Subject:  Policy on Excess Emissions During Startup, Shutdown, Maintenance, and Malfunctions, September 28, 1982.

Letter from Kathleen M. Bennett, Assistant Administrator for Air, Noise and Radiation, to Regional Administrators, Regions I-X, Subject:  Policy on Excess Emissions During Startup, Shutdown, Maintenance, and Malfunctions, February 15, 1983.

Letter from John B. Rasnic, Director, Stationary Source Compliance Division, Office of Air Quality Planning and Standards, to Linda M. Murphy, Director, Air, Pesticides and Toxics Management Division, Region 1, Subject:  Automatic or Blanket Exemptions for Excess Emissions During Startup and Shutdowns Under PSD, January 28, 1993.

James A. Jahnke, Continuous Emission Monitoring, 2nd Ed., John Wiley & Sons, Inc., New York, 2000, at p. 241.

Id. at 241-242.

California Air Pollution Control Officers Association (CAPCOA), Air Toxics "Hot Spots" Program Revised 1992 Risk Assessment Guidelines, October 1993.

www.oehha.ca.gov.

Gas Research Institute (GRI), Gas-Fired Boiler and Turbine Air Toxics Summary Report, Final Report, August 1996.

There is no actual condition in the PDOC limiting startups to the levels shown in Table B-5. Proposed condition 24 sets maximum daily emissions limits, which are calculated in Table B-13. Table B-13 is based on 2 cold starts and two hot starts (one each per turbine) in a single day. If market conditions reduce the number of hours of full load operation or duct burner operation, CCPP could operate with more than 832 hours per year being startup hours and not be in violation of any proposed permit condition.  To avoid the negative implications of repeated startups for toxics emissions, CVRP recommends that the assumed limits of one hot and one cold start per day (Table B-13) and 260 hot starts and 52 cold starts per year per turbine (Table B-5) be made into permit conditions.

The factor of 146, which is based on annual emissions, takes into account reduced fuel use during partial load operation.

Formaldehyde emissions adjusted to account for partial load operation = [(0.11)(832 hr)(146) + (0.11)(7928)]/8760 = 1.625.  The increase in emissions is 1.625/0.11 = 14.77.

Increase in formaldehyde cancer risk due to partial load operation = (1.05x10-2 ug/m3)(6.0x10-6)(11.3) = 9.31x10-7.

Engineering-Science, Inc., Air Toxic Emissions Testing of a Natural Gas Fired Turbine at Sycamore Cogeneration Company, Bakersfield,  California, June 30, 1992.

Acute RELs are found at www.oehha.ca.gov/air/acute_rels/allAcRELs.html.  Chronic RELs are found at www.oehha.ca.gov/air/chronic_rels/AllChrels.html.

The Applicant argues that this change "would not affect the determination that the acute hazard index is well below 1.0."  (Metcalf Response to Staff Data Request PH-1, 4/7/00, p. 2).  However, this does not appear to be correct.  The revised acute REL is given by: 0.33 - 0.284 + 0.284(2.37x10-2/6.43x10-3) = 1.05.

Letter from Dennis Jang, BAAQMD, to Ken Abreu, March 2, 2000.

California Air Resources Board, Development of Toxics Emission Factors from Source Test Data Collected under the Air Toxics Hot Spots Program:  Volume 1, Final Report, April 1996.

Letter from William V. Loscutoff, Chief, Monitoring and Laboratory Division,  to All Air Pollution Control Officers/Executive Officers, Re: Advisories to Limit the Use of ARB Method 430 (M430) Determination of Formaldehyde and Acetaldehyde in Emissions from Stationary Sources, April 28, 2000.

R.R. Freeman, (Air Toxics Ltd, 916-985-1000), The Analysis of Acrolein Using CARB Method 430: What Works and What Doesn't Work, A&WMA Proceedings, 1993.

CARB, Emission Inventory Criteria and Guidelines Report for the Air Toxics "Hot Spots" Program, May 15, 1999, p. 56.

CARE’s complaint may be viewed at the web site http://www.calfree.com/OCRDelta.html.

CARB California Emissions Inventory Data http://www.arb.ca.gov/EMISINV/maps/statemap/cntymap.htm